Version: 1.0
Base URL: http://<PDU-IP>:8000
Example PDU IP: 192.168.250.105

1. Authentication API

Purpose

The Authentication API is used by the software tool to authenticate with the PDU and obtain an access token.

The access token must be used for subsequent protected API requests.

API

Method: POST
Endpoint:  /api/v1/auth

Request

Content-Type: application/json

Example:

{

"username": "admin",

"password": "password"

}

Sample API Call

curl -X POST http://192.168.250.105:8000/api/v1/auth \

-H "Content-Type: application/json" \

-d '{

"username": "admin",

"password": "password"

}'

Successful Response

HTTP Status: 200 OK

{

"access_token": "eyJhbGciOiJIUzI1NiIs...",

"token_type": "bearer"

}

Response Fields

| Field | Description |
| --- | --- |
| access_token | JWT access token generated after successful authentication |
| token_type | Authentication type. Normally bearer |

Using the Token

The returned token should be included in the Authorization header for protected APIs.

Authorization: Bearer <access_token>

Example:

curl http://192.168.250.105:8000/api/v1/status \

-H "Authorization: Bearer eyJhbGciOiJIUzI1NiIs..."

2. Configuration API

Purpose

The Configuration API is used to configure PDU communication parameters.

This API is primarily intended for configuring the PDU's MQTT/network-related configuration.

API

Method: POST
Endpoint:

/api/v1/config

Request

Example:

{

"mqtt_broker": "192.168.250.10",

"mqtt_port": 1883,

"mqtt_username": "pdu_user",

"mqtt_password": "pdu_password"

}

Sample API Call

curl -X POST http://192.168.250.105:8000/api/v1/config \

-H "Content-Type: application/json" \

-H "Authorization: Bearer <access_token>" \

-d '{

"mqtt_broker": "192.168.250.10",

"mqtt_port": 1883,

"mqtt_username": "pdu_user",

"mqtt_password": "pdu_password"

}'

Successful Response

Example:

{

"status": "Configuration updated successfully"

}

Notes

- The configuration request must contain the required configuration parameters.

- The access token should be supplied in the Authorization header.

- The PDU applies the new configuration after successful validation.

- Exact configuration fields can be extended in future API versions without changing the overall API structure.

3. PDU Status API

Purpose

The Status API provides the current basic operating status of the PDU, including battery information and system/load information.

API

Method: GET
Endpoint: /api/v1/status

Sample API Call

curl -X GET http://192.168.250.105:8000/api/v1/status \

-H "Authorization: Bearer <access_token>"

Successful Response

HTTP Status: 200 OK

{

"hostname": "TESTPDU001",

"mac_address": "00:11:22:33:44:55",

"timestamp": 1723540000,

"battery_percentage": 85,

"battery_state": "Discharging",

"system_voltage": 48.2,

"load_current": 2.5,

"battery_charging_current": 10.0,

"battery_capacity_in_min": 120,

"time_since_boot_in_sec": 86400

}

Response Fields

| Field | Description | Example |
| --- | --- | --- |
| hostname | PDU hostname/device name | TESTPDU001 |
| mac_address | PDU network MAC address | 00:11:22:33:44:55 |
| timestamp | Time when status was generated | 1723540000 |
| battery_percentage | Current battery state of charge | 85 |
| battery_state | Current battery operating state | Discharging |
| system_voltage | Current system/bus voltage in volts | 48.2 |
| load_current | Current load consumption in amperes | 2.5 |
| battery_charging_current | Battery charging current in amperes | 10.0 |
| battery_capacity_in_min | Estimated remaining battery runtime in minutes | 120 |
| time_since_boot_in_sec | Time elapsed since PDU boot in seconds | 86400 |

Possible Battery States

Typical values are:

Charging

Ready

Discharging

The software tool should treat battery_state as a string and should not assume that only these three values will exist in future versions.

4. Remote Shutdown API

Purpose

The Remote Shutdown API allows the software tool to remotely shut down the PDU/load.

This is a control API and should only be called after successful authentication.

API

Method: POST
Endpoint:  /api/v1/remote-shutdown

Request

Content-Type: application/json

Example:

{

"username": "admin"

}

The username identifies the user/tool requesting the remote shutdown.

Sample API Call

curl -X POST http://192.168.250.105:8000/api/v1/remote-shutdown \

-H "Content-Type: application/json" \

-H "Authorization: Bearer <access_token>" \

-d '{

"username": "admin"

}'

Successful Response

HTTP Status: 200 OK

{

"username": "admin",

"shutoff": true,

"timestamp": 1723540000,

"status": "Remote shutdown executed"

}

Response Fields

| Field | Description |
| --- | --- |
| username | User who requested the shutdown |
| shutoff | Indicates that the shutdown command was executed |
| timestamp | Time when the shutdown command was executed |
| status | Result/status message |

Example Response

{

"username": "admin",

"shutoff": true,

"timestamp": 1723540000,

"status": "Remote shutdown executed"

}

API Summary

| API | Method | Endpoint | Purpose |
| --- | --- | --- | --- |
| Authentication | POST | /api/v1/auth | Authenticate and obtain access token |
| Configuration | POST | /api/v1/config | Configure PDU parameters |
| Status | GET | /api/v1/status | Read current PDU/battery status |
| Remote Shutdown | POST | /api/v1/remote-shutdown | Execute remote shutdown |

Typical Software Tool Flow

The software tool should normally communicate with the PDU in the following sequence:

1. Authenticate

2. Receive access_token

3. Send Configuration

4. Read PDU Status

5. Perform Remote Shutdown when required

For protected APIs:

Authorization: Bearer <access_token>

Decoder : visics

Example Complete Sequence

Step 1 — Login

POST /api/v1/auth

Request:

{

"username": "admin",

"password": "password"

}

Response:

{

"access_token": "eyJhbGciOiJIUzI1NiIs...",

"token_type": "bearer"

}

Step 2 — Read Status

GET /api/v1/status

Header:

Authorization: Bearer eyJhbGciOiJIUzI1NiIs...

Response:

{

"hostname": "TESTPDU001",

"mac_address": "00:11:22:33:44:55",

"timestamp": 1723540000,

"battery_percentage": 85,

"battery_state": "Discharging",

"system_voltage": 48.2,

"load_current": 2.5,

"battery_charging_current": 0.0,

"battery_capacity_in_min": 120,

"time_since_boot_in_sec": 86400

}

Step 3 — Remote Shutdown

POST /api/v1/remote-shutdown

Request:

{

"username": "admin"

}

Response:

{

"username": "admin",

"shutoff": true,

"timestamp": 1723540000,

"status": "Remote shutdown executed"

}

Authentication Requirement

| API | Authentication |
| --- | --- |
| /api/v1/auth | Not required |
| /api/v1/config | Bearer token |
| /api/v1/status | Bearer token |
| /api/v1/remote-shutdown | Bearer token |